## Sheet1
SELECTION OF MACHINE
S.NO | Room Name | TR (w.r.t) Calculation | CFM (w.r.t) Calculation | Rounded CFM | TR (w.r.t) 1TR=400cfm(Rounded CFM divided by 400) | Max.TR
1 | Bedroom 1 | 2.12 | 1419.6 | 1420 | 3.55 | 3.55
2 | Living Room | 3.27 | 1847.54 | 1850 | 4.62 | 4.62
3 | Bedroom 2 | 2.04 | 1397.56 | 1400 | 3.5 | 3.5
4 | Master Bedroom | 2.03 | 1465.6 | 1470 | 3.56 | 3.56
5 | Dining Room | 3.1 | 1732.5 | 1730 | 4.32 | 4.32
| Window AC (or) Split AC | Ductable Split/VRV/Package | A.H.U. | FCU | CHILLER | COOLING TOWER
| 2.5 TR | Sum of Total Maximum TR = 19.55 TR Approx 20 TR | Total Rounded CFM = 7870 , TR = 7870/400 = 19.67 TR Approx.= 20 TR | FCU 1 => 1420cfm appx = 1400cfm So, We can use 3.5 TR | For AHU, AHU = 20 TR, Chiller 20TR x 2 No. | Cooling Tower: For Air Water System : AHU+FCU= 20+21=41TR GPM=41x3=123
| 1.5TR and 2 TR |  |  | FCU 2 => 1850cfm appx = 2000cfm So, We can use 5 TR
| 2 TR |  |  | FCU 3 => 1400cfm We can use 3.5 TR | For FCU, FCU= 20.5 TR, Chiller 21 TR x 2 No.
| 2 TR |  |  | FCU 4 => 1470cfm appx = 1600cfm So, We can use 4 TR
| 1.5 TR and 2 TR |  |  | FCU 5 => 1730cfm appx = 1800cfm So, We can use 4.5 TR |  | For Air Cooled Chiller, Cooling Tower not Required
Note:- For Air Cooled Chiller, Cooling Tower in not required.
if we are using both AHU + FCU then we can use chiller as Let AHU 20TR & FCU 21TR so Total TR= 41 then used chiller 41TRx2no.